## REAL
Tabela de Registradores - MYSQL ¦ SM6 MT SE ENG¦ IP: 10.0.1.2 DS:
REGISTRADOR | ID | DATAPOINT | OFFSET | DASHBOARD
SepamS20_262_Ia Phase Current [A] | 149 | DP_955765 | 262 | Diagrama Unifilar (big number) ¦ Analytics media tensao [ grafico, max/min (big number)
SepamS20_263_Ib Phase Current [A] | 150 | DP_045007 | 263 | Diagrama Unifilar (big number) ¦ Analytics media tensao [ grafico, max/min (big number)
SepamS20_264_Ic Phase Current [A] | 151 | DP_544849 | 264 | Diagrama Unifilar (big number) ¦ Analytics media tensao [ grafico, max/min (big number)
SepamS20_265_Ir Residual Current [A] | 152 | DP_379397 | 265 | Diagrama Unifilar (big number) ¦ Analytics media tensao [ grafico, max/min (big number)
SepamS20_266_Ia Average Phase Current [A] | 153 | DP_310091 | 266
SepamS20_267_Ib Average Phase Current [A] | 154 | DP_698448 | 267
SepamS20_268_Ic Average Phase Current [A] | 155 | DP_590054 | 268
SepamS20_276_Ia Peak Demand Phase Current [A] | 156 | DP_687619 | 276 | Analytics media tensao [ big number ]
SepamS20_277_Ib Peak Demand Phase Current [A] | 157 | DP_906374 | 277 | Analytics media tensao [ big number ]
SepamS20_278_Ic Peak Demand Phase Current [A] | 158 | DP_363472 | 278 | Analytics media tensao [ big number ]
SepamS20_280_Trip Ia Tripping Current [A] | 159 | DP_421000 | 280 | Analytics media tensao [ big number ]
SepamS20_281_Trip Ib Tripping Current [A] | 160 | DP_084724 | 281 | Analytics media tensao [ big number ]
SepamS20_282_Trip Ic Tripping Current [A] | 161 | DP_179438 | 282 | Analytics media tensao [ big number ]
SepamS20_283_Trip Ir Tripping Current [A] | 162 | DP_366830 | 283 | Analytics media tensao [ big number ]
SepamS20_284_Cumulative Breaking Current [A] | 163 | DP_714095 | 284
SepamS20_285_Number of Operations | 164 | DP_610371 | 285 | Analytics media tensao [ big number ]
SepamS20_286_Operating Time [ms] | 165 | DP_431056 | 286 | Analytics media tensao [ big number ]
SepamS20_287_Charging Time [s] | 166 | DP_880667 | 287 | Analytics media tensao [ big number ]
SepamS20_289_Running Hours Counter [h] | 167 | DP_922981 | 289 | Analytics media tensao [ big number ]
SepamS20_290_Thermal Capacity Used [%] | 168 | DP_962012 | 290
SepamS20_291_Operating Time Before Overload Tripping [min] | 169 | DP_297959 | 291
SepamS20_292_Waiting Time After Overload Tripping [min] | 170 | DP_603063 | 292
SepamS20_293_Unbalance Ratio [%IB] | 171 | DP_846176 | 293
SepamS20_294_Starting Time/Overload [s] | 172 | DP_444015 | 294
SepamS20_295_Starting Current Overload [A] | 173 | DP_939334 | 295
SepamS20_296_Block Start Time Delay [min] | 174 | DP_386972 | 296
SepamS20_297_Number of Starts Allowed | 175 | DP_611617 | 297 | Analytics media tensao [ big number ]
Barra_sup_energ | 176 | DP_315607 |  | Diagrama Unifilar [barramento superior energizado = 1, barramento desenergizado = 0]
Tabela de Registradores - MYSQL ¦ SM6 BT SEE ENG - José Roberto ¦ SEE ENG BT Trafo 1¦ IP: 10.0.1.2 DS:
REGISTRADOR | ID | DATAPOINT | OFFSET | DASHBOARD
Schneider-PM1200_(01)_3913_Current Average [A] | 177 | DP_388321 | 3912
Schneider-PM1200_(02)_3929_Current Phase 1 [A] | 178 | DP_204876 | 3928 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao corrente [ grafico, gauge, max e min ]
Schneider-PM1200_(03)_3943_Current Phase 2 [A] | 179 | DP_620887 | 3942 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao corrente [ grafico, gauge, max e min ]
Schneider-PM1200_(04)_3957_Current Phase 3 [A] | 180 | DP_255457 | 3956 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao corrente [ grafico, gauge, max e min ]
Schneider-PM1200_(05)_3909_Line to Line Average Voltage [V] | 181 | DP_502007 | 3908
Schneider-PM1200_(06)_3911_Line to Neutral Voltage [V] | 182 | DP_788151 | 3910
Schneider-PM1200_(07)_3925_Voltage Phase 1 to Phase 2 [V] | 183 | DP_442119 | 3924 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(08)_3939_Voltage Phase 2 to Phase 3 [V] | 184 | DP_049453 | 3938 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(09)_3953_Voltage Phase 3 to Phase 1 [V] | 185 | DP_042094 | 3952 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(10)_3927_Voltage Phase 1 to Neutral [V] | 186 | DP_514344 | 3926 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(11)_3941_Voltage Phase 2 to Neutral [V] | 187 | DP_947545 | 3940 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(12)_3955_Voltage Phase 3 to Neutral [V] | 188 | DP_343080 | 3954 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(13)_3903_Active Power Total [W] | 189 | DP_627089 | 3902 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(14)_3919_Active Power Phase 1 [W] | 190 | DP_243943 | 3918 | Analytics baixa tensao potência [ grafico linha, grafico barra, big number ]
Schneider-PM1200_(15)_3933_Active Power Phase 2 [W] | 191 | DP_977609 | 3932 | Analytics baixa tensao potência [ grafico linha, grafico barra, big number ]
Schneider-PM1200_(16)_3947_Active Power Phase 3 [W] | 192 | DP_123289 | 3946 | Analytics baixa tensao potência [ grafico linha, grafico barra, big number ]
Schneider-PM1200_(17)_3905_Reactive Power Total [VAr] | 193 | DP_345943 | 3904
Schneider-PM1200_(18)_3921_Reactive Power Phase 1 [VAr] | 194 | DP_367174 | 3920 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(19)_3935_Reactive Power Phase 2 [VAr] | 195 | DP_780612 | 3934 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(20)_3949_Reactive Power Phase 3 [VAr] | 196 | DP_026227 | 3948 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(21)_3901_Apparent Power Total [VA] | 197 | DP_936616 | 3900
Schneider-PM1200_(22)_3917_Apparent Power Phase 1 [VA] | 198 | DP_680744 | 3916 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(23)_3931_Apparent Power Phase 2 [VA] | 199 | DP_656565 | 3930 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(24)_3945_Apparent Power Phase 3 [VA] | 200 | DP_406303 | 3944 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(25)_3907_Power Factor Average | 201 | DP_204850 | 3906
Schneider-PM1200_(26)_3923_Power Factor Phase 1 | 202 | DP_195725 | 3922 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(27)_3937_Power Factor Phase 2 | 203 | DP_022733 | 3936 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(28)_3951_Power Factor Phase 3 | 204 | DP_532442 | 3950 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(29)_3915_Frequency [Hz] | 205 | DP_438625 | 3914 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(30)_3861_Voltage THD Phase 1 [%] | 206 | DP_852220 | 3860
Schneider-PM1200_(31)_3863_Voltage THD Phase 2 [%] | 207 | DP_771723 | 3862
Schneider-PM1200_(32)_3865_Voltage THD Phase 3 [%] | 208 | DP_738164 | 3864
Schneider-PM1200_(33)_3867_Current THD Phase 1 [%] | 209 | DP_744862 | 3866
Schneider-PM1200_(34)_3869_Current THD Phase 2 [%] | 210 | DP_603931 | 3868
Schneider-PM1200_(35)_3871_Current THD Phase 3 [%] | 211 | DP_393235 | 3870
Schneider-PM1200_(36)_3959_Forward Apparent Energy [VAh] | 212 | DP_454387 | 3958
Schneider-PM1200_(37)_3961_Forward Active Energy [Wh] | 213 | DP_174915 | 3960 | Analytics baixa tensao consumo de energia [ big number ]
Schneider-PM1200_(38)_3963_Forward Reactive Inductive Energy [VArh] | 214 | DP_551022 | 3962
Schneider-PM1200_(39)_3965_Forward Reactive Capacitive Energy [VArh] | 215 | DP_421208 | 3964
Schneider-PM1200_(40)_3967_Reverse Apparent Energy [VAh] | 216 | DP_243929 | 3966
Schneider-PM1200_(41)_3969_Reverse Active Energy [Wh] | 217 | DP_790072 | 3968 | Analytics baixa tensao consumo de energia [ big number ]
Schneider-PM1200_(42)_3971_Reverse Reactive Inductive Energy [VArh] | 218 | DP_118995 | 3970
Schneider-PM1200_(43)_3973_Reverse Reactive Capacitive Energy [VArh] | 219 | DP_553877 | 3972
Schneider-PM1200_(44)_3979_Maximum Demand [W] | 220 | DP_478623 | 3978
Barra_inf_Energ | 221 | DP_958363 |  | Diagrama Unifilar [barramento inferior energizado = 1, barramento desenergizado = 0]

## SIMULADO
Tabela de Registradores - MYSQL ¦ SM6 MT SE ENG¦ IP: 10.0.1.2 DS:
REGISTRADOR | ID | DATAPOINT | OFFSET | DASHBOARD
SepamS20_262_Ia Phase Current [A] | 1 | DP_955765 | 262 | Diagrama Unifilar (big number) ¦ Analytics media tensao [ grafico, max/min (big number)
SepamS20_263_Ib Phase Current [A] | 2 | DP_045007 | 263 | Diagrama Unifilar (big number) ¦ Analytics media tensao [ grafico, max/min (big number)
SepamS20_264_Ic Phase Current [A] | 3 | DP_544849 | 264 | Diagrama Unifilar (big number) ¦ Analytics media tensao [ grafico, max/min (big number)
SepamS20_265_Ir Residual Current [A] | 4 | DP_379397 | 265 | Diagrama Unifilar (big number) ¦ Analytics media tensao [ grafico, max/min (big number)
SepamS20_266_Ia Average Phase Current [A] | 5 | DP_310091 | 266
SepamS20_267_Ib Average Phase Current [A] | 6 | DP_698448 | 267
SepamS20_268_Ic Average Phase Current [A] | 7 | DP_590054 | 268
SepamS20_276_Ia Peak Demand Phase Current [A] | 8 | DP_687619 | 276 | Analytics media tensao [ big number ]
SepamS20_277_Ib Peak Demand Phase Current [A] | 9 | DP_906374 | 277 | Analytics media tensao [ big number ]
SepamS20_278_Ic Peak Demand Phase Current [A] | 10 | DP_363472 | 278 | Analytics media tensao [ big number ]
SepamS20_280_Trip Ia Tripping Current [A] | 11 | DP_421000 | 280 | Analytics media tensao [ big number ]
SepamS20_281_Trip Ib Tripping Current [A] | 12 | DP_084724 | 281 | Analytics media tensao [ big number ]
SepamS20_282_Trip Ic Tripping Current [A] | 13 | DP_179438 | 282 | Analytics media tensao [ big number ]
SepamS20_283_Trip Ir Tripping Current [A] | 14 | DP_366830 | 283 | Analytics media tensao [ big number ]
SepamS20_284_Cumulative Breaking Current [A] | 15 | DP_714095 | 284
SepamS20_285_Number of Operations | 16 | DP_610371 | 285 | Analytics media tensao [ big number ]
SepamS20_286_Operating Time [ms] | 17 | DP_431056 | 286 | Analytics media tensao [ big number ]
SepamS20_287_Charging Time [s] | 18 | DP_880667 | 287 | Analytics media tensao [ big number ]
SepamS20_289_Running Hours Counter [h] | 19 | DP_922981 | 289 | Analytics media tensao [ big number ]
SepamS20_290_Thermal Capacity Used [%] | 20 | DP_962012 | 290
SepamS20_291_Operating Time Before Overload Tripping [min] | 21 | DP_297959 | 291
SepamS20_292_Waiting Time After Overload Tripping [min] | 22 | DP_603063 | 292
SepamS20_293_Unbalance Ratio [%IB] | 23 | DP_846176 | 293
SepamS20_294_Starting Time/Overload [s] | 24 | DP_444015 | 294
SepamS20_295_Starting Current Overload [A] | 25 | DP_939334 | 295
SepamS20_296_Block Start Time Delay [min] | 26 | DP_386972 | 296
SepamS20_297_Number of Starts Allowed | 27 | DP_611617 | 297 | Analytics media tensao [ big number ]
Barra_sup_energ | 73 | DP_315607 |  | Diagrama Unifilar [barramento superior energizado = 1, barramento desenergizado = 0]
Tabela de Registradores - MYSQL ¦ SM6 BT SEE ENG - José Roberto ¦ SEE ENG BT Trafo 1¦ IP: 10.0.1.2 DS:
REGISTRADOR | ID | DATAPOINT | OFFSET | DASHBOARD
Schneider-PM1200_(01)_3913_Current Average [A] | 28 | DP_388321 | 3912
Schneider-PM1200_(02)_3929_Current Phase 1 [A] | 29 | DP_204876 | 3928 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao corrente [ grafico, gauge, max e min ]
Schneider-PM1200_(03)_3943_Current Phase 2 [A] | 30 | DP_620887 | 3942 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao corrente [ grafico, gauge, max e min ]
Schneider-PM1200_(04)_3957_Current Phase 3 [A] | 31 | DP_255457 | 3956 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao corrente [ grafico, gauge, max e min ]
Schneider-PM1200_(05)_3909_Line to Line Average Voltage [V] | 32 | DP_502007 | 3908
Schneider-PM1200_(06)_3911_Line to Neutral Voltage [V] | 33 | DP_788151 | 3910
Schneider-PM1200_(07)_3925_Voltage Phase 1 to Phase 2 [V] | 34 | DP_442119 | 3924 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(08)_3939_Voltage Phase 2 to Phase 3 [V] | 35 | DP_049453 | 3938 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(09)_3953_Voltage Phase 3 to Phase 1 [V] | 36 | DP_042094 | 3952 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(10)_3927_Voltage Phase 1 to Neutral [V] | 37 | DP_514344 | 3926 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(11)_3941_Voltage Phase 2 to Neutral [V] | 38 | DP_947545 | 3940 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(12)_3955_Voltage Phase 3 to Neutral [V] | 39 | DP_343080 | 3954 | Diagrama Unifilar (big number) ¦ Analytics baixa tensao tensão [ grafico, max e min ]
Schneider-PM1200_(13)_3903_Active Power Total [W] | 40 | DP_627089 | 3902 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(14)_3919_Active Power Phase 1 [W] | 41 | DP_243943 | 3918 | Analytics baixa tensao potência [ grafico linha, grafico barra, big number ]
Schneider-PM1200_(15)_3933_Active Power Phase 2 [W] | 42 | DP_977609 | 3932 | Analytics baixa tensao potência [ grafico linha, grafico barra, big number ]
Schneider-PM1200_(16)_3947_Active Power Phase 3 [W] | 43 | DP_123289 | 3946 | Analytics baixa tensao potência [ grafico linha, grafico barra, big number ]
Schneider-PM1200_(17)_3905_Reactive Power Total [VAr] | 44 | DP_345943 | 3904
Schneider-PM1200_(18)_3921_Reactive Power Phase 1 [VAr] | 45 | DP_367174 | 3920 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(19)_3935_Reactive Power Phase 2 [VAr] | 46 | DP_780612 | 3934 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(20)_3949_Reactive Power Phase 3 [VAr] | 47 | DP_026227 | 3948 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(21)_3901_Apparent Power Total [VA] | 48 | DP_936616 | 3900
Schneider-PM1200_(22)_3917_Apparent Power Phase 1 [VA] | 49 | DP_680744 | 3916 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(23)_3931_Apparent Power Phase 2 [VA] | 50 | DP_656565 | 3930 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(24)_3945_Apparent Power Phase 3 [VA] | 51 | DP_406303 | 3944 | Analytics baixa tensao potência [ grafico barra ]
Schneider-PM1200_(25)_3907_Power Factor Average | 52 | DP_204850 | 3906
Schneider-PM1200_(26)_3923_Power Factor Phase 1 | 53 | DP_195725 | 3922 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(27)_3937_Power Factor Phase 2 | 54 | DP_022733 | 3936 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(28)_3951_Power Factor Phase 3 | 55 | DP_532442 | 3950 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(29)_3915_Frequency [Hz] | 56 | DP_438625 | 3914 | Analytics baixa tensao potência [ big number ]
Schneider-PM1200_(30)_3861_Voltage THD Phase 1 [%] | 57 | DP_852220 | 3860
Schneider-PM1200_(31)_3863_Voltage THD Phase 2 [%] | 58 | DP_771723 | 3862
Schneider-PM1200_(32)_3865_Voltage THD Phase 3 [%] | 59 | DP_738164 | 3864
Schneider-PM1200_(33)_3867_Current THD Phase 1 [%] | 60 | DP_744862 | 3866
Schneider-PM1200_(34)_3869_Current THD Phase 2 [%] | 61 | DP_603931 | 3868
Schneider-PM1200_(35)_3871_Current THD Phase 3 [%] | 62 | DP_393235 | 3870
Schneider-PM1200_(36)_3959_Forward Apparent Energy [VAh] | 63 | DP_454387 | 3958
Schneider-PM1200_(37)_3961_Forward Active Energy [Wh] | 64 | DP_174915 | 3960 | Analytics baixa tensao consumo de energia [ big number ]
Schneider-PM1200_(38)_3963_Forward Reactive Inductive Energy [VArh] | 65 | DP_551022 | 3962
Schneider-PM1200_(39)_3965_Forward Reactive Capacitive Energy [VArh] | 66 | DP_421208 | 3964
Schneider-PM1200_(40)_3967_Reverse Apparent Energy [VAh] | 67 | DP_243929 | 3966
Schneider-PM1200_(41)_3969_Reverse Active Energy [Wh] | 68 | DP_790072 | 3968 | Analytics baixa tensao consumo de energia [ big number ]
Schneider-PM1200_(42)_3971_Reverse Reactive Inductive Energy [VArh] | 69 | DP_118995 | 3970
Schneider-PM1200_(43)_3973_Reverse Reactive Capacitive Energy [VArh] | 70 | DP_553877 | 3972
Schneider-PM1200_(44)_3979_Maximum Demand [W] | 71 | DP_478623 | 3978
Barra_inf_Energ | 72 | DP_958363 |  | Diagrama Unifilar [barramento inferior energizado = 1, barramento desenergizado = 0]